The Site Book   thesitebook.co.uk	BLANK TEMPLATE

# Hot work permit

Blank permit for one hot work task, in one place, for one work period. Includes a pre-start checklist and a fire watch record.

Hot work is any process that produces flames, sparks or heat, such as welding, cutting, grinding, soldering and torch-on roofing. Use a cold method instead where you can.

Where hot work cannot be avoided, control it with a permit. Issue each permit for a defined job, place and time period. Never issue a blanket permit for hot work anywhere on site or over several days.

Check with your insurer whether the Joint Code of Practice applies to your project. Where it does, all hot work needs a permit once fitting-out has started on site and in any building being refurbished, and each permit is signed off at the end of its work period.

# Permit details

| Permit number |  | Issuing company |  |
| --- | --- | --- | --- |
| Site address |  | Building, floor and room |  |
| Exact location of the work |  | Type of hot work |  |
| Equipment to be used |  | Person in direct control of the work |  |
| Company doing the work |  | How to raise the alarm |  |
| Valid from (date and time) |  | Valid until (date and time) |  |

# Before work starts

The person doing the work checks each item at the work site before starting, and the issuer confirms it. If an item cannot be met, do not start.

| Check | Yes | N/A | Notes |
| --- | --- | --- | --- |
| Loose combustible material removed from the work area, from below it, and from gaps in walls, floors and ceilings that heat or sparks could reach |  |  |  |
| The other side of any wall or partition being worked on checked and cleared |  |  |  |
| Combustible material that cannot be moved, and any openings, protected with non-combustible board or blankets |  |  |  |
| Work area screened when welding, cutting or grinding |  |  |  |
| Flammable liquids removed from the area |  |  |  |
| At least two suitable fire extinguishers within reach of the work and the fire watch position |  |  |  |
| People doing the work and the fire watch know how to raise the alarm and the way out |  |  |  |
| Any fire detection isolated for the work is limited to the work zone, with someone named to reinstate it |  |  |  |
| Hot work equipment checked and in good repair, and gas cylinders secured |  |  |  |
| Gas detector or thermal imaging camera in use, where appropriate |  |  |  |

# Fire watch

Keep a careful watch for fire while the work is going on and during breaks, including places the work could affect that cannot be seen from the work area.

After the hot work ends, keep a continuous fire watch for at least an hour, then make at least one more check two hours after the work ended. Finish hot work at least two hours before the end of the working day so there is time for these checks.

Where the Joint Code applies, after the first hour make further checks at intervals of no more than 20 minutes for at least another hour. Include areas within 10 metres on the other side of walls, partitions and ceilings, and floors below.

| Fire watch carried out by |  | Hot work finished at (time) |  |
| --- | --- | --- | --- |
| Continuous fire watch ended at (time) |  | Final check at (time) |  |

| Time | Areas checked | Findings | Initials |
| --- | --- | --- | --- |

# Issue and acceptance

Only someone with clearly assigned authority issues or closes this permit. The person in charge of the work signs to accept it and briefs everyone doing the work. If the work carries on into another work period, issue a fresh permit.

|  | Name | Signature | Date and time |
| --- | --- | --- | --- |
| Issued by |  |  |  |
| Accepted by (person in charge of the work) |  |  |  |

# Close-out

Before the permit is closed, check the work area and every area sparks or heat could have reached, including floors above and below and the other side of walls.

| Check | Done | Notes |
| --- | --- | --- |
| Work area and nearby areas free of smouldering material and flames |  |  |
| Hot waste, such as welding rod ends, removed safely |  |  |
| Any isolated fire detection reinstated |  |  |
| Equipment and gas cylinders moved to a safe place |  |  |
| Photos or thermal images from the fire watch attached |  |  |

|  | Name | Signature | Date and time |
| --- | --- | --- | --- |
| Work finished: person in charge of the work |  |  |  |
| Permit closed by issuer |  |  |  |

Based on: HSE guidance HSG168, Fire safety in construction (third edition, 2022), paragraphs 118 to 132; the Fire Protection Association's Joint Code of Practice, Fire Prevention on Construction Sites (10th edition incorporating Amendments 1 and 2), sections 2 and 16 and Annex A; HSE guidance HSG250 on permit-to-work systems.

HSE, Fire safety in construction (HSG168, third edition): https://www.hse.gov.uk/pubns/books/hsg168.htm

Fire Protection Association, Fire Prevention on Construction Sites: the Joint Code of Practice, 10th edition incorporating Amendments 1 and 2: https://www.thefpa.co.uk/resource-download/858

HSE, Guidance on permit-to-work systems (HSG250): https://www.hse.gov.uk/pubns/books/hsg250.htm

Blank template from The Site Book, October 2026. Fill it in for the actual job and site.